## Make Ready Report
Operation Number | Attachment Action (I)nstalling (R)emoving (E)xisting | Pole Owner | Pole # | Pole Structure | Proposed Riser (Yes/No) & QTY | Proposed Guy (Yes/No) & QTY | PLA (%) with proposed attachment | Construction Grade of Analysis | Existing Mid-Span Data |  | Make Ready Data
[9 empty] | Height Lowest Com | Height Lowest CPS Electrical | Attacher Description | Attachment Height |  | Mid-Span (same span as existing) Proposed
[12 empty] | Existing | Proposed | Proposed
1 | (I)nstalling | CPS Energy | PL410620 | 40-4 | No | No | 82.20% | C | 14 ft 9 in | 25 ft 8 in | CPS ENERGY Neutral | 29'-6" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 27'-12" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 23'-7" | N/A | N/A
[11 empty] | AT&T Telco Com | 22'-4" | N/A | N/A
[11 empty] | AT&T Com Drop | 21'-5" | N/A | N/A
[11 empty] | Charter Fiber Optic Com | 24'-7" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL410620 | PL398491 |  |  |  | 18 ft 8 in
2 | (I)nstalling | CPS Energy | PL398491 | 45-2 Southern Pine | Yes | Yes | 61.49% | C | 15 ft 1 in | 24 ft 8 in | AT&T Com Drop | 19'-8" | N/A | N/A
[11 empty] | CPS ENERGY Service | 27'-1" | N/A | N/A
[11 empty] | AT&T Com Drop | 19'-6" | N/A | N/A
[11 empty] | AT&T Com Drop | 19'-6" | N/A | N/A
[11 empty] | CPS ENERGY Neutral | 27'-1" | N/A | N/A
[11 empty] | CPS ENERGY Neutral | 26'-11" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 25'-6" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 21'-4" | N/A | N/A
[11 empty] | AT&T Telco Com | 20'-4" | N/A | N/A
[11 empty] | AT&T Com Drop | 19'-8" | N/A | N/A
[11 empty] | Charter Fiber Optic Com | 22'-4" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 25'-9" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL398491 | PL401451 |  |  |  | 15 ft 3 in
3 | (I)nstalling | CPS Energy | PL389359 | 45-4 Southern Pine | Yes | Yes | 92.00% | C | N/A | N/A | CPS ENERGY Neutral | 27'-3" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 25'-9" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 22'-8" | N/A | N/A
[11 empty] | AT&T Telco Com | 21'-8" | N/A | N/A
[11 empty] | CPS ENERGY Neutral | 27'-3" | N/A | N/A
[11 empty] | Charter Fiber Optic Com | 22'-12" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL389359 | N/A |  |  |  | 18 ft 8 in
4 | (I)nstalling | CPS Energy | PL404474 | 40-3 Southern Pine | No | No | 62.45% | C | 19 ft 6 in | 25 ft 6 in | CPS ENERGY Neutral | 25'-12" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 24'-6" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 22'-9" | N/A | N/A
[11 empty] | AT&T Telco Com | 21'-7" | N/A | N/A
[11 empty] | CPS ENERGY Street Light Feed | 25'-12" | N/A | N/A
[11 empty] | Charter Fiber Optic Com | 21'-7" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL404474 | PL900997 |  |  |  | 18 ft 8 in
5 | (I)nstalling | CPS Energy | PL900997 | 45-2 Southern Pine | Yes | Yes | 64.17% | C | 20 ft 12 in | 26 ft 5 in | CPS ENERGY Neutral | 27'-1" | N/A | N/A
[11 empty] | CPS ENERGY Street Light Feed | 27'-1" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 25'-10" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 21'-6" | N/A | N/A
[11 empty] | AT&T Telco Com | 20'-6" | N/A | N/A
[11 empty] | CPS ENERGY Service | 27'-1" | N/A | N/A
[11 empty] | Charter Fiber Optic Com | 21'-6" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL900997 | PL398490 |  |  |  | 15 ft 3 in
6 | (I)nstalling | CPS Energy | PL370858 | 45-2 Southern Pine | Yes | Yes | 41.95% | C | 19 ft 4 in | 24 ft 7 in | CPS ENERGY Neutral | 26'-6" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 25'-5" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 22'-10" | N/A | N/A
[11 empty] | AT&T Telco Com | 21'-10" | N/A | N/A
[11 empty] | Charter Fiber Optic Com | 22'-1" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL370858 | PL379971 |  |  |  | 18 ft 8 in
7 | (I)nstalling | CPS Energy | PL379971 | 40-4 Southern Pine | No | No | 83.34% | N/A | 19 ft 4 in | 24 ft 7 in | CPS ENERGY Neutral | 26'-4" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 24'-9" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 23'-9" | N/A | N/A
[11 empty] | AT&T Telco Com | 22'-9" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL379971 | PL370858
8 | (I)nstalling | CPS Energy | PL379966 | 45-4 | Yes | Yes | 89.74% | N/A | 18 ft 8 in | 23 ft 9 in | CPS ENERGY Neutral | 27'-7" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 26'-4" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 23'-7" | N/A | N/A
[11 empty] | AT&T Telco Com | 22'-7" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL379966 | PL379971
9 | (I)nstalling | CPS Energy | PL373937 | 55-3 Southern Pine | No | No | Replace/Repair Crossarm% | N/A | 22 ft 3 in | 31 ft 3 in | CPS ENERGY Neutral | 38'-8" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 36'-8" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 32'-8" | N/A | N/A
[11 empty] | AT&T Telco Com | 27'-6" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 36'-5" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL373937 | PL379966
10 | (I)nstalling | CPS Energy | PL404475 | 55-3 Southern Pine | No | No | 78.54% | N/A | 28 ft 8 in | 36 ft 5 in | CPS ENERGY Neutral | 38'-7" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 37'-1" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 31'-5" | N/A | N/A
[11 empty] | AT&T Telco Com | 21'-1" | N/A | N/A
[11 empty] | CPS ENERGY Neutral | 36'-1" | N/A | N/A
[11 empty] | CPS ENERGY Neutral | 36'-1" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 36'-10" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL404475 | PL373937
11 | (I)nstalling | CPS Energy | PL373935 | 45-4 | No | No | 80.86% | N/A | 15 ft 3 in | 30 ft 10 in | CPS ENERGY Neutral | 29'-3" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 27'-9" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 24'-10" | N/A | N/A
[11 empty] | AT&T Telco Com | 23'-12" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL373935 | PL404475
12 | (I)nstalling | CPS Energy | PL398490 | 50-1 Southern Pine | No | No | 51.03% | N/A | 17 ft 5 in | 25 ft 4 in | CPS ENERGY Neutral | 27'-2" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 26'-0" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 24'-10" | N/A | N/A
[11 empty] | AT&T Telco Com | 23'-11" | N/A | N/A
[11 empty] | CPS ENERGY Street Light Feed | 27'-2" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL398490 | PL373935
13 | (I)nstalling | CPS Energy | PL401451 | 40-4 | No | No | 95.28% | N/A | 15 ft 1 in | 24 ft 8 in | CPS ENERGY Neutral | 26'-7" | N/A | N/A
[11 empty] | CPS ENERGY Supply Fiber | 24'-11" | N/A | N/A
[11 empty] | AT&T Fiber Optic Com | 22'-6" | N/A | N/A
[11 empty] | AT&T Telco Com | 21'-3" | N/A | N/A
[9 empty] | From Pole | To Pole
[9 empty] | PL401451 | PL398491
14 | (I)nstalling | CPS Energy | PL410595 | 40-5 | No | No | N/A | N/A | 14 ft 5 in | 27 ft 1 in
[9 empty] | From Pole | To Pole
[9 empty] | PL410595 | PL410620